## HeatingActualData
This data comes straight from a manufacturers data sheet
The data is at constant air flow/temp, so correction factors are provided
This data is ready to paste directly into the parameter estimation tool

30 TON WATER-WATER HEAT PUMP HEATING MODE					Airflow Correction
Water Side EWT	Water Side Flow	Air Side EWT DB	Air Side Flow Rate	Total Capacity	Power Usage			AirFlow Multiplier	Total Capacity	Power Usage
F	GPM	F	CFM	MBTUH	kW			Decimal	Multiplier	Multiplier
20	2	68	300	3.9	0.4			0.6	0.933	1.216
30	1	68	300	4.7	0.4			0.72	0.957	1.124
30	1.5	68	300	4.9	0.4			0.8	0.973	1.072
30	2	68	300	5	0.4			0.88	0.984	1.037
40	1	68	300	5.6	0.5			0.96	0.995	1.01
40	1.5	68	300	5.8	0.5			1	1	1
40	2	68	300	5.9	0.5			1.04	1.005	0.993
50	1	68	300	6.3	0.5			1.12	1.012	0.986
50	1.5	68	300	6.6	0.5			1.2	1.019	0.99
50	2	68	300	6.7	0.5
60	1	68	300	7	0.5			Enter Air Temp Correction
60	1.5	68	300	7.3	0.5			AirTemp	Capacity	Power Usage
60	2	68	300	7.4	0.5			deg F	Multiplier	Multiplier
70	1	68	300	7.7	0.5			45	1.032	0.777
70	1.5	68	300	8	0.5			50	1.029	0.817
70	2	68	300	8.1	0.5			55	1.025	0.859
80	1	68	300	8.4	0.5			60	1.018	0.903
80	1.5	68	300	8.8	0.5			65	1.01	0.95
80	2	68	300	9	0.5			70	1	1
90	1	68	300	9.2	0.5			75	0.988	1.052
90	1.5	68	300	9.7	0.5			80	0.974	1.107
90	2	68	300	10	0.5			120	1.019	0.99

					Rated Air Flow	300	CFM
					Rated Water Flow	1.5	GPM
					Rated Total Capacity	6	MBTUH
					Rated Compressor Power	0.5	kW

## HeatingKnownParameters
This data is generated by first making up fake curve coefficients
The idea here is that once the curve is evaluated to come up with an artificial dataset, the parameter tool should be able to recreate the original coefficients
This data is ready to paste directly into the parameter estimation tool

	MADE UP COEFFICIENTS; THESE ARE THE OUTPUT OF THE CALCULATION TOOL				MADE UP INDEPENDENT VARIABLES					SCALING INDEPENDENT VARIABLES					CALCULATE SCALED Q and P			UNSCALE Q and P TO REAL VALUES			FINAL DATA SET READY TO PASTE IN TO THE TOOL
	Params	Capacity	Power		Water EWT	Water Flow	Air EWT	Air Flow		Scaled Water EWT	Scaled Water Flow	Scaled Air EWT	Scaled Air Flow		Capacity Curve Output	Power Curve Output		Capacity	Power		Water EWT	Water Flow	Air EWT	Air Flow	Capacity	Power
	A	15.1	92.8		C	m3/s	C	m3/s		-	-	-	-		-	-		kW	kW		C	m3/s	C	m3/s	kW	kW
	B	63.5	64.6		1	1	1	1		0.968727915194346	0.05	0.968727915194346	0.1		125.119540636042	198.173975265018		12511.9540636042	9908.69876325088		1	1	1	1	12511.9540636042	9908.69876325088
	C	42.2	38.4		2	2	2	2		0.97226148409894	0.1	0.97226148409894	0.2		133.118038869258	204.132932862191		13311.8038869258	10206.6466431095		2	2	2	2	13311.8038869258	10206.6466431095
	D	50.1	7.2		3	3	3	3		0.975795053003533	0.15	0.975795053003533	0.3		141.116537102473	210.091890459364		14111.6537102473	10504.5945229682		3	3	3	3	14111.6537102473	10504.5945229682
	E	52.3	97.5		4	4	4	4		0.979328621908127	0.2	0.979328621908127	0.4		149.115035335689	216.050848056537		14911.5035335689	10802.5424028269		4	4	4	4	14911.5035335689	10802.5424028269
					5	5	5	1		0.982862190812721	0.25	0.982862190812721	0.1		137.073533568905	219.12980565371		13707.3533568905	10956.4902826855		5	5	5	1	13707.3533568905	10956.4902826855
	MADE UP RATED PARAMETERS				6	6	6	2		0.986395759717314	0.3	0.986395759717314	0.2		145.07203180212	225.088763250883		14507.203180212	11254.4381625442		6	6	6	2	14507.203180212	11254.4381625442
	Rated Air Flow	10	m3/s		7	7	7	3		0.989929328621908	0.35	0.989929328621908	0.3		153.070530035336	231.047720848056		15307.0530035336	11552.3860424028		7	7	7	3	15307.0530035336	11552.3860424028
	Rated Water Flow	20	m3/s		8	8	8	4		0.993462897526502	0.4	0.993462897526502	0.4		161.069028268551	237.00667844523		16106.9028268551	11850.3339222615		8	8	8	4	16106.9028268551	11850.3339222615
	Rated Heating Capacity	100	kW		9	9	1	1		0.996996466431095	0.45	0.968727915194346	0.1		147.232473498233	238.259487632509		14723.2473498233	11912.9743816254		9	9	1	1	14723.2473498233	11912.9743816254
	Rated Compressor Power	50	kW		10	10	2	2		1.00053003533569	0.5	0.97226148409894	0.2		155.230971731449	244.218445229682		15523.0971731449	12210.9222614841		10	10	2	2	15523.0971731449	12210.9222614841
					11	11	3	3		1.00406360424028	0.55	0.975795053003533	0.3		163.229469964664	250.177402826855		16322.9469964664	12508.8701413428		11	11	3	3	16322.9469964664	12508.8701413428
	THIS IS SPECIFIED BY E+				12	12	4	4		1.00759717314488	0.6	0.979328621908127	0.4		171.22796819788	256.136360424028		17122.796819788	12806.8180212014		12	12	4	4	17122.796819788	12806.8180212014
	Internally Rated Temp in K:	283	K		13	13	5	1		1.01113074204947	0.65	0.982862190812721	0.1		159.186466431095	259.215318021201		15918.6466431095	12960.7659010601		13	13	5	1	15918.6466431095	12960.7659010601
					14	14	6	2		1.01466431095406	0.7	0.986395759717314	0.2		167.184964664311	265.174275618374		16718.4964664311	13258.7137809187		14	14	6	2	16718.4964664311	13258.7137809187
					15	15	7	3		1.01819787985866	0.75	0.989929328621908	0.3		175.183462897526	271.133233215548		17518.3462897526	13556.6616607774		15	15	7	3	17518.3462897526	13556.6616607774
Model Formulation:					16	16	8	4		1.02173144876325	0.8	0.993462897526502	0.4		183.181961130742	277.092190812721		18318.1961130742	13854.609540636		16	16	8	4	18318.1961130742	13854.609540636
Q = Q_rated * (A + B*TL + C*TS + D*VL + E*VS)					17	1	1	1		1.02526501766784	0.05	0.968727915194346	0.1		127.505406360424	200.345		12750.5406360424	10017.25		17	1	1	1	12750.5406360424	10017.25
					18	2	2	2		1.02879858657244	0.1	0.97226148409894	0.2		135.50390459364	206.303957597173		13550.390459364	10315.1978798587		18	2	2	2	13550.390459364	10315.1978798587
					19	3	3	3		1.03233215547703	0.15	0.975795053003533	0.3		143.502402826855	212.262915194346		14350.2402826855	10613.1457597173		19	3	3	3	14350.2402826855	10613.1457597173
					20	4	4	4		1.03586572438163	0.2	0.979328621908127	0.4		151.500901060071	218.221872791519		15150.0901060071	10911.093639576		20	4	4	4	15150.0901060071	10911.093639576
					21	5	5	1		1.03939929328622	0.25	0.982862190812721	0.1		139.459399293286	221.300830388693		13945.9399293286	11065.0415194346		21	5	5	1	13945.9399293286	11065.0415194346
					22	6	6	2		1.04293286219081	0.3	0.986395759717314	0.2		147.457897526502	227.259787985866		14745.7897526502	11362.9893992933		22	6	6	2	14745.7897526502	11362.9893992933
					23	7	7	3		1.04646643109541	0.35	0.989929328621908	0.3		155.456395759717	233.218745583039		15545.6395759717	11660.9372791519		23	7	7	3	15545.6395759717	11660.9372791519
					24	8	8	4		1.05	0.4	0.993462897526502	0.4		163.454893992933	239.177703180212		16345.4893992933	11958.8851590106		24	8	8	4	16345.4893992933	11958.8851590106
					25	9	1	1		1.05353356890459	0.45	0.968727915194346	0.1		149.618339222615	240.430512367491		14961.8339222615	12021.5256183746		25	9	1	1	14961.8339222615	12021.5256183746
					26	10	2	2		1.05706713780919	0.5	0.97226148409894	0.2		157.61683745583	246.389469964664		15761.683745583	12319.4734982332		26	10	2	2	15761.683745583	12319.4734982332
					27	11	3	3		1.06060070671378	0.55	0.975795053003533	0.3		165.615335689046	252.348427561837		16561.5335689046	12617.4213780919		27	11	3	3	16561.5335689046	12617.4213780919
					28	12	4	4		1.06413427561837	0.6	0.979328621908127	0.4		173.613833922261	258.307385159011		17361.3833922261	12915.3692579505		28	12	4	4	17361.3833922261	12915.3692579505
					29	13	5	1		1.06766784452297	0.65	0.982862190812721	0.1		161.572332155477	261.386342756184		16157.2332155477	13069.3171378092		29	13	5	1	16157.2332155477	13069.3171378092
					30	14	6	2		1.07120141342756	0.7	0.986395759717314	0.2		169.570830388693	267.345300353357		16957.0830388693	13367.2650176678		30	14	6	2	16957.0830388693	13367.2650176678
					31	15	7	3		1.07473498233216	0.75	0.989929328621908	0.3		177.569328621908	273.30425795053		17756.9328621908	13665.2128975265		31	15	7	3	17756.9328621908	13665.2128975265
					32	16	8	4		1.07826855123675	0.8	0.993462897526502	0.4		185.567826855124	279.263215547703		18556.7826855124	13963.1607773852		32	16	8	4	18556.7826855124	13963.1607773852

## CoolingActualData
This data comes straight from a manufacturers data sheet
The data is at constant air temp/flow, so it includes correction factors for airflow rate and entering air db/wb
This data is ready to paste directly into the parameter estimation tool

30 TON WATER-WATER HEAT PUMP COOLING MODE					Airflow Correction
Water Side EWT	Water Side Flow	Air Side EWT-DB	Air Side EWT-WB	Air Side Flow Rate	Total Capacity	Sensible Capacity	Power Usage			AirFlow Multiplier	Total Capacity	Sensible Capacity	Power Usage
F	GPM	F	F	CFM	MBTUH	MBTUH	kW			Decimal	Multiplier	Multiplier	Multiplier
30	1	80.6	66.2	300	6.9	5	0.3			0.6	0.907	0.878	0.936
30	1.5	80.6	66.2	300	7.1	5	0.3			0.72	0.942	0.925	0.951
30	2	80.6	66.2	300	7.2	5.1	0.3			0.8	0.963	0.954	0.966					Rated Air Flow	300	CFM
40	1	80.6	66.2	300	7.2	5.3	0.3			0.88	0.979	0.974	0.977					Rated Water Flow	1.5	GPM
40	1.5	80.6	66.2	300	7.2	5.3	0.3			0.96	0.994	0.992	0.992					Rated Total Capacity	6	MBTUH
40	2	80.6	66.2	300	7.3	5.3	0.3			1	1	1	1					Rated Sensible Capacity	5	MBTUH
50	1	80.6	66.2	300	7.1	5.5	0.3			1.04	1.006	1.007	1.009					Rated Compressor Power	0.5	kW
50	1.5	80.6	66.2	300	7.2	5.5	0.3			1.12	1.015	1.017	1.027
50	2	80.6	66.2	300	7.3	5.5	0.3			1.2	1.022	1.023	1.047
60	1	80.6	66.2	300	6.9	5.6	0.4					ORIGINAL DB/WB CORRECTION FACTOR AS DISPLAYED IN CATALOG
60	1.5	80.6	66.2	300	7.1	5.6	0.3			Enter Air Temp Correction					DB Temp
60	2	80.6	66.2	300	7.1	5.7	0.3			DryBulb	WetBulb	TotalCap	SensibleCap	Power			WB	TotalCap	60	65	70	75	80	85	90	95	100	Power
70	1	80.6	66.2	300	6.5	5.5	0.4			deg F	deg F	Multiplier	Multiplier	Multiplier			45	0.6634	*	*	*	*	*	*	*	*	0.9856
70	1.5	80.6	66.2	300	6.8	5.6	0.4			60	50	0.7399	0.7663	0.9889			50	0.7399	0.7663	*	*	*	*	*	*	*	*	0.9889
70	2	80.6	66.2	300	6.9	5.6	0.4			60	55	0.8164	0.5937	0.9921			55	0.8164	0.5937	0.8724	1.0816	*	*	*	*	*	*	0.9921
80	1	80.6	66.2	300	6.1	5.3	0.4			65	55	0.8164	0.8724	0.9921			60	0.8929		0.6709	0.8826	1.1211	*	*	*	*	*	0.9954
80	1.5	80.6	66.2	300	6.3	5.4	0.4			70	55	0.8164	1.0816	0.9921			65	0.9694			0.6624	0.885	1.0986	*	*	*	*	0.9987
80	2	80.6	66.2	300	6.4	5.5	0.4			65	60	0.8929	0.6709	0.9954			67	1			0.5685	0.7879	1	1.1891	1.3838	*	*	1
90	1	80.6	66.2	300	5.6	5.1	0.5			70	60	0.8929	0.8826	0.9954			70	1.0459				0.6391	0.8521	1.0361	1.2347	1.4461	*	1.002
90	1.5	80.6	66.2	300	5.8	5.2	0.5			75	60	0.8929	1.1211	0.9954			75	1.1224					0.6056	0.7783	0.9861	1.2256	1.469	1.0052
90	2	80.6	66.2	300	6	5.3	0.5			70	65	0.9694	0.6624	0.9987
100	1	80.6	66.2	300	5.1	4.8	0.6			75	65	0.9694	0.885	0.9987
100	1.5	80.6	66.2	300	5.3	4.9	0.5			80	65	0.9694	1.0986	0.9987
100	2	80.6	66.2	300	5.4	5	0.5			70	67	1	0.5685	1
110	1	80.6	66.2	300	4.5	4.4	0.6			75	67	1	0.7879	1
110	1.5	80.6	66.2	300	4.8	4.6	0.6			80	67	1	1	1
110	2	80.6	66.2	300	4.9	4.6	0.6			85	67	1	1.1891	1
120	1	80.6	66.2	300	4.1	4.1	0.7			90	67	1	1.3838	1
120	1.5	80.6	66.2	300	4.3	4.2	0.6			75	70	1.0459	0.6391	1.002
120	2	80.6	66.2	300	4.4	4.3	0.6			80	70	1.0459	0.8521	1.002
					85	70	1.0459	1.0361	1.002
					90	70	1.0459	1.2347	1.002
					95	70	1.0459	1.4461	1.002
					80	75	1.1224	0.6056	1.0052
					85	75	1.1224	0.7783	1.0052
					90	75	1.1224	0.9861	1.0052
					95	75	1.1224	1.2256	1.0052
					100	75	1.1224	1.469	1.0052

## CoolingKnownParameters
This data is generated by first making up fake curve coefficients
The idea here is that once the curve is evaluated to come up with an artificial dataset, the parameter tool should be able to recreate the original coefficients
This data is ready to paste directly into the parameter estimation tool

	MADE UP COEFFICIENTS; THESE ARE THE OUTPUT OF THE CALCULATION TOOL					MADE UP INDEPENDENT VARIABLES					SCALING INDEPENDENT VARIABLES					CALCULATE SCALED Q and P				UNSCALE Q and P TO REAL VALUES				FINAL DATA SET READY TO PASTE IN TO THE TOOL
	Params	Capacity	Sensible	Power		Water EWT	Water Flow	Air EWT DB	Air EWT WB	Air Flow		Scaled Water EWT	Scaled Water Flow	Scaled Air EWT DB	Scaled Air EWT WB	Scaled Air Flow		Capacity Curve Output	Sensible Curve Output	Power Curve Output		Capacity	Sensible	Power		Water EWT	Water Flow	Air EWT DB	Air EWT WB	Air Flow	Capacity	Sensible	Power
	A	81.4	62.5	97.4		C	m3/s	C	C	m3/s		-	-	-	-	-		-	-	-		kW	kW	kW		C	m3/s	C	C	m3/s	kW	kW	kW
	B	69.2	10.4	64.3		1	1	1	1	1		0.968727915194346	0.05	0.968727915194346	0.968727915194346	0.1		232.934275618375	127.035088339223	198.799134275618		23293.4275618375	10162.8070671378	3975.98268551237		1	1	1	1	1	23293.4275618375	10162.8070671378	3975.98268551237
	C	76.8	18.5	31.5		2	2	2	2	2		0.97226148409894	0.1	0.97226148409894	0.97226148409894	0.2		243.550176678445	140.800954063604	207.732650176678		24355.0176678445	11264.0763250883	4154.65300353357		2	2	2	2	2	24355.0176678445	11264.0763250883	4154.65300353357
	D	54.1	23.7	38.7		3	3	3	3	1		0.975795053003533	0.15	0.975795053003533	0.975795053003533	0.1		243.346077738516	135.666819787986	208.926166077739		24334.6077738516	10853.3455830389	4178.52332155477		3	3	3	3	1	24334.6077738516	10853.3455830389	4178.52332155477
	E	93.8	94.5	94.5		4	4	4	4	2		0.979328621908127	0.2	0.979328621908127	0.979328621908127	0.2		253.961978798586	149.432685512368	217.859681978799		25396.1978798587	11954.6148409894	4357.19363957597		4	4	4	4	2	25396.1978798587	11954.6148409894	4357.19363957597
	F		82.6			5	5	5	1	1		0.982862190812721	0.25	0.982862190812721	0.968727915194346	0.1		252.779787985866	144.037067137809	218.144363957597		25277.9787985866	11522.9653710247	4362.88727915194		5	5	5	1	1	25277.9787985866	11522.9653710247	4362.88727915194
					6	6	6	2	2		0.986395759717314	0.3	0.986395759717314	0.97226148409894	0.2		263.395689045936	157.802932862191	227.077879858657		26339.5689045936	12624.2346289753	4541.55759717315		6	6	6	2	2	26339.5689045936	12624.2346289753	4541.55759717315
	MADE UP RATED PARAMETERS					7	7	7	3	1		0.989929328621908	0.35	0.989929328621908	0.975795053003533	0.1		263.191590106007	152.668798586572	228.271395759717		26319.1590106007	12213.5038869258	4565.42791519435		7	7	7	3	1	26319.1590106007	12213.5038869258	4565.42791519435
	Rated Air Flow	10	m3/s			8	8	8	4	2		0.993462897526502	0.4	0.993462897526502	0.979328621908127	0.2		273.807491166078	166.434664310954	237.204911660777		27380.7491166078	13314.7731448763	4744.09823321555		8	8	8	4	2	27380.7491166078	13314.7731448763	4744.09823321555
	Rated Water Flow	20	m3/s			9	9	1	1	1		0.996996466431095	0.45	0.968727915194346	0.968727915194346	0.1		272.625300353357	160.745053003534	237.489593639576		27262.5300353357	12859.6042402827	4749.79187279152		9	9	1	1	1	27262.5300353357	12859.6042402827	4749.79187279152
	Rated Total Capacity	100	kW			10	10	2	2	2		1.00053003533569	0.5	0.97226148409894	0.97226148409894	0.2		283.241201413428	174.510918727915	246.423109540636		28324.1201413428	13960.8734982332	4928.46219081272		10	10	2	2	2	28324.1201413428	13960.8734982332	4928.46219081272
	Rated Sensible Capacity	80	kW			11	11	3	3	1		1.00406360424028	0.55	0.975795053003533	0.975795053003533	0.1		283.037102473498	169.376784452297	247.616625441696		28303.7102473498	13550.1427561837	4952.33250883392		11	11	3	3	1	28303.7102473498	13550.1427561837	4952.33250883392
	Rated Compressor Power	20	kW			12	12	4	4	2		1.00759717314488	0.6	0.979328621908127	0.979328621908127	0.2		293.653003533569	183.142650176678	256.550141342756		29365.3003533569	14651.4120141343	5131.00282685512		12	12	4	4	2	29365.3003533569	14651.4120141343	5131.00282685512
					13	13	5	1	1		1.01113074204947	0.65	0.982862190812721	0.968727915194346	0.1		292.470812720848	177.74703180212	256.834823321555		29247.0812720848	14219.7625441696	5136.6964664311		13	13	5	1	1	29247.0812720848	14219.7625441696	5136.6964664311
	THIS IS SPECIFIED BY E+					14	14	6	2	2		1.01466431095406	0.7	0.986395759717314	0.97226148409894	0.2		303.086713780919	191.512897526502	265.768339222615		30308.6713780919	15321.0318021201	5315.3667844523		14	14	6	2	2	30308.6713780919	15321.0318021201	5315.3667844523
	Internally Rated Temp in K:	283	K			15	15	7	3	1		1.01819787985866	0.75	0.989929328621908	0.975795053003533	0.1		302.882614840989	186.378763250883	266.961855123675		30288.2614840989	14910.3010600707	5339.2371024735		15	15	7	3	1	30288.2614840989	14910.3010600707	5339.2371024735
					16	16	8	4	2		1.02173144876325	0.8	0.993462897526502	0.979328621908127	0.2		313.49851590106	200.144628975265	275.895371024735		31349.851590106	16011.5703180212	5517.9074204947		16	16	8	4	2	31349.851590106	16011.5703180212	5517.9074204947
					17	1	1	1	1		1.02526501766784	0.05	0.968727915194346	0.968727915194346	0.1		237.276325088339	128.375017667845	200.580053003534		23727.6325088339	10270.0014134276	4011.60106007067		17	1	1	1	1	23727.6325088339	10270.0014134276	4011.60106007067
Model Formulation:					18	2	2	2	2		1.02879858657244	0.1	0.97226148409894	0.97226148409894	0.2		247.89222614841	142.140883392226	209.513568904594		24789.222614841	11371.2706713781	4190.27137809187		18	2	2	2	2	24789.222614841	11371.2706713781	4190.27137809187
Q = Q_rated * (A + B*Twb + C*TS + D*VL + E*VS)					19	3	3	3	1		1.03233215547703	0.15	0.975795053003533	0.975795053003533	0.1		247.688127208481	137.006749116608	210.707084805654		24768.8127208481	10960.5399293286	4214.14169611307		19	3	3	3	1	24768.8127208481	10960.5399293286	4214.14169611307
Q_s = Q_s,rated *(A+B*Twb+C*Tdb+D*Ts+E*VL+F*VS)					20	4	4	4	2		1.03586572438163	0.2	0.979328621908127	0.979328621908127	0.2		258.304028268551	150.772614840989	219.640600706714		25830.4028268551	12061.8091872792	4392.81201413428		20	4	4	4	2	25830.4028268551	12061.8091872792	4392.81201413428
P = P_rated * (A + B*Twb + C*TS + D*VL + E*VS)					21	5	5	1	1		1.03939929328622	0.25	0.982862190812721	0.968727915194346	0.1		257.12183745583	145.376996466431	219.925282685512		25712.183745583	11630.1597173145	4398.50565371025		21	5	5	1	1	25712.183745583	11630.1597173145	4398.50565371025
					22	6	6	2	2		1.04293286219081	0.3	0.986395759717314	0.97226148409894	0.2		267.737738515901	159.142862190813	228.858798586572		26773.7738515901	12731.428975265	4577.17597173145		22	6	6	2	2	26773.7738515901	12731.428975265	4577.17597173145
					23	7	7	3	1		1.04646643109541	0.35	0.989929328621908	0.975795053003533	0.1		267.533639575972	154.008727915194	230.052314487633		26753.3639575972	12320.6982332156	4601.04628975265		23	7	7	3	1	26753.3639575972	12320.6982332156	4601.04628975265
					24	8	8	4	2		1.05	0.4	0.993462897526502	0.979328621908127	0.2		278.149540636042	167.774593639576	238.985830388693		27814.9540636042	13421.9674911661	4779.71660777385		24	8	8	4	2	27814.9540636042	13421.9674911661	4779.71660777385
					25	9	1	1	1		1.05353356890459	0.45	0.968727915194346	0.968727915194346	0.1		276.967349823322	162.084982332155	239.270512367491		27696.7349823322	12966.7985865724	4785.41024734982		25	9	1	1	1	27696.7349823322	12966.7985865724	4785.41024734982
					26	10	2	2	2		1.05706713780919	0.5	0.97226148409894	0.97226148409894	0.2		287.583250883392	175.850848056537	248.204028268551		28758.3250883392	14068.067844523	4964.08056537103		26	10	2	2	2	28758.3250883392	14068.067844523	4964.08056537103
					27	11	3	3	1		1.06060070671378	0.55	0.975795053003533	0.975795053003533	0.1		287.379151943463	170.716713780919	249.397544169611		28737.9151943463	13657.3371024735	4987.95088339223		27	11	3	3	1	28737.9151943463	13657.3371024735	4987.95088339223
					28	12	4	4	2		1.06413427561837	0.6	0.979328621908127	0.979328621908127	0.2		297.995053003534	184.4825795053	258.331060070671		29799.5053003534	14758.606360424	5166.62120141343		28	12	4	4	2	29799.5053003534	14758.606360424	5166.62120141343
					29	13	5	1	1		1.06766784452297	0.65	0.982862190812721	0.968727915194346	0.1		296.812862190813	179.086961130742	258.61574204947		29681.2862190813	14326.9568904594	5172.3148409894		29	13	5	1	1	29681.2862190813	14326.9568904594	5172.3148409894
					30	14	6	2	2		1.07120141342756	0.7	0.986395759717314	0.97226148409894	0.2		307.428763250883	192.852826855124	267.54925795053		30742.8763250883	15428.2261484099	5350.9851590106		30	14	6	2	2	30742.8763250883	15428.2261484099	5350.9851590106
					31	15	7	3	1		1.07473498233216	0.75	0.989929328621908	0.975795053003533	0.1		307.224664310954	187.718692579505	268.74277385159		30722.4664310954	15017.4954063604	5374.8554770318		31	15	7	3	1	30722.4664310954	15017.4954063604	5374.8554770318
					32	16	8	4	2		1.07826855123675	0.8	0.993462897526502	0.979328621908127	0.2		317.840565371025	201.484558303887	277.67628975265		31784.0565371025	16118.764664311	5553.525795053		32	16	8	4	2	31784.0565371025	16118.764664311	5553.525795053