## HeatingActualData
This data comes straight from a manufacturers data sheet
The data includes columns for load side flows at 45, 67, and 90.
The full data could be pasted in full, but in this case, a correction factor was estimated for flow correction
This data is ready to paste directly into the parameter estimation tool

30 TON WATER-WATER HEAT PUMP HEATING MODE					LoadSideFlowCorrection
Source Side EWT	Source Side Flow	Load Side EWT	Load Side Flow Rate	Total Capacity	Power Usage			Load Side Flow Rate	Total Capacity	Power Usage
F	GPM	F	GPM	MBTUH	kW			GPM	Multiplier	Multiplier
30	45	100	45	301.1	27.73			67	1.012	0.94
30	67	80	45	319.5	22.14			90	1.018	0.91
30	67	100	45	307.4	27.86
30	67	120	45	295.7	35.49
30	90	60	45	338.9	17.81
30	90	80	45	323.5	22.2
30	90	100	45	310.5	27.92
30	90	120	45	297.8	35.55				Rated Load Flow	50	GPM
40	45	60	45	374.5	18.3				Rated Source Flow	50	GPM
40	45	80	45	358.8	22.75				Rated Total Capacity	360	MBTUH
40	45	100	45	344.9	28.58				Rated Compressor Power	30	kW
40	45	120	45	330.3	36.35
40	67	60	45	389.3	18.51
40	67	80	45	370.6	22.94
40	67	100	45	353.9	28.75
40	67	120	45	336.5	36.51
40	90	60	45	396.5	18.61
40	90	80	45	376.2	23.03
40	90	100	45	358.2	28.84
40	90	120	45	339.5	36.58
50	45	60	45	430.1	19.11
50	45	80	45	410.6	23.6
50	45	100	45	392.7	29.51
50	45	120	45	372.9	37.39
50	67	60	45	450.4	19.43
50	67	80	45	426.9	23.88
50	67	100	45	405.2	29.76
50	67	120	45	381.6	37.61
50	90	60	45	460.3	19.59
50	90	80	45	434.7	24.02
50	90	100	45	433.2	29.89
50	90	120	45	385.7	37.71
60	45	60	45	489.5	20.07
60	45	80	45	466.3	24.59
60	45	100	45	444.3	30.58
60	45	120	45	419	38.56
60	67	60	45	516.8	20.55
60	67	80	45	488.2	25.01
60	67	100	45	461.1	30.95
60	67	120	45	430.7	38.87
60	90	60	45	530.1	20.79
60	90	80	45	498.8	25.22
60	90	100	45	469.3	31.14
60	90	120	45	436.3	39.03
70	45	60	45	552.4	21.2
70	45	80	45	525.5	25.76
70	45	100	45	499.2	31.83
70	67	60	45	588	21.91
70	67	80	45	554.2	26.38
70	67	100	45	521.5	32.38
70	90	60	45	605.6	22.28
70	90	80	45	568.2	26.7
70	90	100	45	532.2	32.66

## HeatingKnownParameters
This data is generated by first making up fake curve coefficients
The idea here is that once the curve is evaluated to come up with an artificial dataset, the parameter tool should be able to recreate the original coefficients
This data is ready to paste directly into the parameter estimation tool

	MADE UP COEFFICIENTS; THESE ARE THE OUTPUT OF THE CALCULATION TOOL				MADE UP INDEPENDENT VARIABLES					SCALING INDEPENDENT VARIABLES					CALCULATE SCALED Q and P			UNSCALE Q and P TO REAL VALUES			FINAL DATA SET READY TO PASTE IN TO THE TOOL
	Params	Capacity	Power		Source Side EWT	Source Side Flow	Load Side EWT	Load Side Flow Rate		Scaled Source Side EWT	Scaled Source Side Flow	Scaled Load Side EWT	Scaled Load Side Flow		Capacity Curve Output	Power Curve Output		Capacity	Power		Source Side EWT	Source Side Flow	Load Side EWT	Load Side Flow Rate	Capacity	Power
	A	12.1	8.1		C	m3/s	C	m3/s		-	-	-	-		-	-		kW	kW		C	m3/s	C	m3/s	kW	kW
	B	31.2	34.8		1	1	1	1		0.968727915194346	0.05	0.968727915194346	0.1		88.0698056537102	99.6437632508834		8806.98056537102	4982.18816254417		1	1	1	1	8806.98056537102	4982.18816254417
	C	34.2	49.5		2	2	2	2		0.97226148409894	0.1	0.97226148409894	0.2		100.915901060071	109.821643109541		10091.5901060071	5491.08215547703		2	2	2	2	10091.5901060071	5491.08215547703
	D	82.1	73.2		3	3	3	3		0.975795053003533	0.15	0.975795053003533	0.3		113.761996466431	119.999522968198		11376.1996466431	5999.97614840989		3	3	3	3	11376.1996466431	5999.97614840989
	E	88.1	51.2		4	4	4	4		0.979328621908127	0.2	0.979328621908127	0.4		126.608091872792	130.177402826855		12660.8091872792	6508.87014134276		4	4	4	4	12660.8091872792	6508.87014134276
					5	5	5	1		0.982862190812721	0.25	0.982862190812721	0.1		106.614187279152	111.075282685512		10661.4187279152	5553.76413427562		5	5	5	1	10661.4187279152	5553.76413427562
	MADE UP RATED PARAMETERS				6	6	6	2		0.986395759717314	0.3	0.986395759717314	0.2		119.460282685512	121.25316254417		11946.0282685512	6062.65812720848		6	6	6	2	11946.0282685512	6062.65812720848
	Rated Load Flow	10	m3/s		7	7	7	3		0.989929328621908	0.35	0.989929328621908	0.3		132.306378091873	131.431042402827		13230.6378091873	6571.55212014134		7	7	7	3	13230.6378091873	6571.55212014134
	Rated Source Flow	20	m3/s		8	8	8	4		0.993462897526502	0.4	0.993462897526502	0.4		145.152473498233	141.608922261484		14515.2473498233	7080.44611307421		8	8	8	4	14515.2473498233	7080.44611307421
	Rated Total Capacity	100	kW		9	9	1	1		0.996996466431095	0.45	0.968727915194346	0.1		124.276590106007	121.523056537102		12427.6590106007	6076.15282685512		9	9	1	1	12427.6590106007	6076.15282685512
	Rated Compressor Power	50	kW		10	10	2	2		1.00053003533569	0.5	0.97226148409894	0.2		137.122685512368	131.70093639576		13712.2685512368	6585.04681978799		10	10	2	2	13712.2685512368	6585.04681978799
					11	11	3	3		1.00406360424028	0.55	0.975795053003533	0.3		149.968780918728	141.878816254417		14996.8780918728	7093.94081272085		11	11	3	3	14996.8780918728	7093.94081272085
	THIS IS SPECIFIED BY E+				12	12	4	4		1.00759717314488	0.6	0.979328621908127	0.4		162.814876325088	152.056696113074		16281.4876325088	7602.83480565371		12	12	4	4	16281.4876325088	7602.83480565371
	Internally Rated Temp in K:	283	K		13	13	5	1		1.01113074204947	0.65	0.982862190812721	0.1		142.820971731449	132.954575971731		14282.0971731449	6647.72879858657		13	13	5	1	14282.0971731449	6647.72879858657
					14	14	6	2		1.01466431095406	0.7	0.986395759717314	0.2		155.667067137809	143.132455830389		15566.7067137809	7156.62279151944		14	14	6	2	15566.7067137809	7156.62279151944
					15	15	7	3		1.01819787985866	0.75	0.989929328621908	0.3		168.51316254417	153.310335689046		16851.316254417	7665.5167844523		15	15	7	3	16851.316254417	7665.5167844523
Model Formulation:					16	16	8	4		1.02173144876325	0.8	0.993462897526502	0.4		181.35925795053	163.488215547703		18135.925795053	8174.41077738516		16	16	8	4	18135.925795053	8174.41077738516
Q = Q_rated * (A + B*TL + C*TS + D*VL + E*VS)					17	1	1	1		1.02526501766784	0.05	0.968727915194346	0.1		90.0033745583039	102.442349823322		9000.33745583039	5122.11749116608		17	1	1	1	9000.33745583039	5122.11749116608
					18	2	2	2		1.02879858657244	0.1	0.97226148409894	0.2		102.849469964664	112.620229681979		10284.9469964664	5631.01148409894		18	2	2	2	10284.9469964664	5631.01148409894
					19	3	3	3		1.03233215547703	0.15	0.975795053003533	0.3		115.695565371025	122.798109540636		11569.5565371025	6139.9054770318		19	3	3	3	11569.5565371025	6139.9054770318
					20	4	4	4		1.03586572438163	0.2	0.979328621908127	0.4		128.541660777385	132.975989399293		12854.1660777385	6648.79946996467		20	4	4	4	12854.1660777385	6648.79946996467
					21	5	5	1		1.03939929328622	0.25	0.982862190812721	0.1		108.547756183746	113.873869257951		10854.7756183746	5693.69346289753		21	5	5	1	10854.7756183746	5693.69346289753
					22	6	6	2		1.04293286219081	0.3	0.986395759717314	0.2		121.393851590106	124.051749116608		12139.3851590106	6202.58745583039		22	6	6	2	12139.3851590106	6202.58745583039
					23	7	7	3		1.04646643109541	0.35	0.989929328621908	0.3		134.239946996466	134.229628975265		13423.9946996466	6711.48144876325		23	7	7	3	13423.9946996466	6711.48144876325
					24	8	8	4		1.05	0.4	0.993462897526502	0.4		147.086042402827	144.407508833922		14708.6042402827	7220.37544169611		24	8	8	4	14708.6042402827	7220.37544169611
					25	9	1	1		1.05353356890459	0.45	0.968727915194346	0.1		126.210159010601	124.321643109541		12621.0159010601	6216.08215547703		25	9	1	1	12621.0159010601	6216.08215547703
					26	10	2	2		1.05706713780919	0.5	0.97226148409894	0.2		139.056254416961	134.499522968198		13905.6254416961	6724.9761484099		26	10	2	2	13905.6254416961	6724.9761484099
					27	11	3	3		1.06060070671378	0.55	0.975795053003533	0.3		151.902349823322	144.677402826855		15190.2349823322	7233.87014134276		27	11	3	3	15190.2349823322	7233.87014134276
					28	12	4	4		1.06413427561837	0.6	0.979328621908127	0.4		164.748445229682	154.855282685512		16474.8445229682	7742.76413427562		28	12	4	4	16474.8445229682	7742.76413427562
					29	13	5	1		1.06766784452297	0.65	0.982862190812721	0.1		144.754540636042	135.75316254417		14475.4540636042	6787.65812720848		29	13	5	1	14475.4540636042	6787.65812720848
					30	14	6	2		1.07120141342756	0.7	0.986395759717314	0.2		157.600636042403	145.931042402827		15760.0636042403	7296.55212014134		30	14	6	2	15760.0636042403	7296.55212014134
					31	15	7	3		1.07473498233216	0.75	0.989929328621908	0.3		170.446731448763	156.108922261484		17044.6731448763	7805.44611307421		31	15	7	3	17044.6731448763	7805.44611307421
					32	16	8	4		1.07826855123675	0.8	0.993462897526502	0.4		183.292826855124	166.286802120141		18329.2826855124	8314.34010600707		32	16	8	4	18329.2826855124	8314.34010600707

## CoolingActualData
This data comes straight from a manufacturers data sheet
The data includes columns for load side flows at 45, 68, and 90.
The full data could be pasted in full, but in this case, a correction factor was estimated for flow correction
This data is ready to paste directly into the parameter estimation tool

30 TON WATER-WATER HEAT PUMP COOLING MODE					LoadSideFlowCorrection
Source Side EWT	Source Side Flow	Load Side EWT	Load Side Flow Rate	Total Capacity	Power Usage			Load Side Flow Rate	Total Capacity	Power Usage
F	GPM	F	GPM	MBTUH	kW			GPM	Multiplier	Multiplier
60	45	40	45	312.4	18.3			68	1.031	1.005
60	45	50	45	365.2	19.11			90	1.046	1.009
60	45	60	45	421.4	20.07
60	45	70	45	480.4	21.2
60	45	80	45	541.5	22.53
60	68	70	45	494.1	19.85
60	68	80	45	558.2	21.02
75	45	40	45	289.6	21.54				Rated Load Flow	50	GPM
75	45	50	45	339.5	22.37				Rated Source Flow	50	GPM
75	45	60	45	392.9	23.34				Rated Total Capacity	360	MBTUH
75	45	70	45	449.1	24.5				Rated Compressor Power	25	kW
75	45	80	45	507.5	25.86
75	68	40	45	296.8	20.48
75	68	50	45	348.9	21.15
75	68	60	45	404.7	21.95
75	68	70	45	463.7	22.91
75	68	80	45	525.3	24.07
75	90	40	45	300.4	19.97
75	90	50	45	353.5	20.56
75	90	60	45	410.5	21.28
75	90	70	45	471	22.16
75	90	80	45	534.2	23.22
90	45	30	45	221.5	24.66
90	45	40	45	264.5	25.45
90	45	50	45	311.3	26.33
90	45	60	45	363.2	27.37
90	45	70	45	416.3	28.58
90	45	80	45	465.1	29.83
90	68	30	45	227.4	23.59
90	68	40	45	272.2	24.2
90	68	50	45	321.3	24.88
90	68	60	45	374.1	25.69
90	68	70	45	430.1	26.66
90	68	80	45	487	27.79
90	90	30	45	230.3	23.07
90	90	40	45	276.1	23.59
90	90	50	45	326.2	24.18
90	90	60	45	380.4	24.89
90	90	70	45	437.9	25.76
90	90	80	45	498.4	26.81
105	45	30	45	198.4	29.44
105	45	40	45	238.1	30.32
105	45	50	45	281.5	31.27
105	45	60	45	328.1	32.37
105	45	70	45	377.5	33.65
105	45	80	45	412.5	34.66
105	68	30	45	204.8	28.13
105	68	40	45	246.5	28.79
105	68	50	45	292.3	29.51
105	68	60	45	341.9	30.35
105	68	70	45	394.6	31.35
105	68	80	45	437.6	32.27
105	90	30	45	208	27.5
105	90	40	45	250.7	28.06
105	90	50	45	297.7	28.67
105	90	60	45	348.6	29.38
105	90	70	45	403.1	30.26
105	90	80	45	450.3	31.12
120	45	30	45	171	35.38
120	45	40	45	206.6	36.35
120	45	50	45	245.7	37.39
120	45	60	45	287.8	38.56
120	45	70	45	332.4	39.91
120	68	30	45	178.2	33.78
120	68	40	45	216	34.51
120	68	50	45	257.8	35.28
120	68	60	45	303.2	36.16
120	68	70	45	351.7	37.2
120	90	30	45	181.7	33
120	90	40	45	220.6	33.62
120	90	50	45	263.7	34.26
120	90	60	45	310.7	35
120	90	70	45	361.1	35.89

## CoolingKnownParameters
This data is generated by first making up fake curve coefficients
The idea here is that once the curve is evaluated to come up with an artificial dataset, the parameter tool should be able to recreate the original coefficients
This data is ready to paste directly into the parameter estimation tool

	MADE UP COEFFICIENTS; THESE ARE THE OUTPUT OF THE CALCULATION TOOL				MADE UP INDEPENDENT VARIABLES					SCALING INDEPENDENT VARIABLES					CALCULATE SCALED Q and P			UNSCALE Q and P TO REAL VALUES			FINAL DATA SET READY TO PASTE IN TO THE TOOL
	Params	Capacity	Power		Source Side EWT	Source Side Flow	Load Side EWT	Load Side Flow Rate		Scaled Source Side EWT	Scaled Source Side Flow	Scaled Load Side EWT	Scaled Load Side Flow		Capacity Curve Output	Power Curve Output		Capacity	Power		Source Side EWT	Source Side Flow	Load Side EWT	Load Side Flow Rate	Capacity	Power
	A	10.2	37.1		C	m3/s	C	m3/s		-	-	-	-		-	-		kW	kW		C	m3/s	C	m3/s	kW	kW
	B	52.3	12.4		1	1	1	1		0.968727915194346	0.05	0.968727915194346	0.1		71.8899293286219	93.5764487632509		7188.99293286219	4678.82243816255		1	1	1	1	7188.99293286219	4678.82243816255
	C	7.5	35.2		2	2	2	2		0.97226148409894	0.1	0.97226148409894	0.2		75.8612367491166	104.10964664311		7586.12367491166	5205.48233215548		2	2	2	2	7586.12367491166	5205.48233215548
	D	12.5	61.2		3	3	3	3		0.975795053003533	0.15	0.975795053003533	0.3		79.8325441696113	114.642844522968		7983.25441696113	5732.14222614841		3	3	3	3	7983.25441696113	5732.14222614841
	E	50.2	84.9		4	4	4	4		0.979328621908127	0.2	0.979328621908127	0.4		83.803851590106	125.176042402827		8380.3851590106	6258.80212014134		4	4	4	4	8380.3851590106	6258.80212014134
					5	5	5	1		0.982862190812721	0.25	0.982862190812721	0.1		82.7751590106007	111.229240282686		8277.51590106007	5561.46201413428		5	5	5	1	8277.51590106007	5561.46201413428
	MADE UP RATED PARAMETERS				6	6	6	2		0.986395759717314	0.3	0.986395759717314	0.2		86.7464664310954	121.762438162544		8674.64664310954	6088.12190812721		6	6	6	2	8674.64664310954	6088.12190812721
	Rated Load Flow	10	m3/s		7	7	7	3		0.989929328621908	0.35	0.989929328621908	0.3		90.7177738515901	132.295636042403		9071.77738515901	6614.78180212014		7	7	7	3	9071.77738515901	6614.78180212014
	Rated Source Flow	20	m3/s		8	8	8	4		0.993462897526502	0.4	0.993462897526502	0.4		94.6890812720848	142.828833922261		9468.90812720848	7141.44169611307		8	8	8	4	9468.90812720848	7141.44169611307
	Rated Total Capacity	100	kW		9	9	1	1		0.996996466431095	0.45	0.968727915194346	0.1		92.1819434628975	128.531501766784		9218.19434628975	6426.57508833922		9	9	1	1	9218.19434628975	6426.57508833922
	Rated Compressor Power	50	kW		10	10	2	2		1.00053003533569	0.5	0.97226148409894	0.2		96.1532508833922	139.064699646643		9615.32508833922	6953.23498233216		10	10	2	2	9615.32508833922	6953.23498233216
					11	11	3	3		1.00406360424028	0.55	0.975795053003533	0.3		100.124558303887	149.597897526502		10012.4558303887	7479.89487632509		11	11	3	3	10012.4558303887	7479.89487632509
	THIS IS SPECIFIED BY E+				12	12	4	4		1.00759717314488	0.6	0.979328621908127	0.4		104.095865724382	160.13109540636		10409.5865724382	8006.55477031802		12	12	4	4	10409.5865724382	8006.55477031802
	Internally Rated Temp in K:	283	K		13	13	5	1		1.01113074204947	0.65	0.982862190812721	0.1		103.067173144876	146.184293286219		10306.7173144876	7309.21466431095		13	13	5	1	10306.7173144876	7309.21466431095
					14	14	6	2		1.01466431095406	0.7	0.986395759717314	0.2		107.038480565371	156.717491166078		10703.8480565371	7835.87455830389		14	14	6	2	10703.8480565371	7835.87455830389
					15	15	7	3		1.01819787985866	0.75	0.989929328621908	0.3		111.009787985866	167.250689045936		11100.9787985866	8362.53445229682		15	15	7	3	11100.9787985866	8362.53445229682
Model Formulation:					16	16	8	4		1.02173144876325	0.8	0.993462897526502	0.4		114.98109540636	177.783886925795		11498.109540636	8889.19434628975		16	16	8	4	11498.109540636	8889.19434628975
Q = Q_rated * (A + B*TL + C*TS + D*VL + E*VS)					17	1	1	1		1.02526501766784	0.05	0.968727915194346	0.1		72.3139575971731	95.566554770318		7231.39575971731	4778.3277385159		17	1	1	1	7231.39575971731	4778.3277385159
					18	2	2	2		1.02879858657244	0.1	0.97226148409894	0.2		76.2852650176678	106.099752650177		7628.52650176678	5304.98763250883		18	2	2	2	7628.52650176678	5304.98763250883
					19	3	3	3		1.03233215547703	0.15	0.975795053003533	0.3		80.2565724381625	116.632950530035		8025.65724381625	5831.64752650177		19	3	3	3	8025.65724381625	5831.64752650177
					20	4	4	4		1.03586572438163	0.2	0.979328621908127	0.4		84.2278798586572	127.166148409894		8422.78798586572	6358.3074204947		20	4	4	4	8422.78798586572	6358.3074204947
					21	5	5	1		1.03939929328622	0.25	0.982862190812721	0.1		83.1991872791519	113.219346289753		8319.91872791519	5660.96731448763		21	5	5	1	8319.91872791519	5660.96731448763
					22	6	6	2		1.04293286219081	0.3	0.986395759717314	0.2		87.1704946996466	123.752544169611		8717.04946996466	6187.62720848057		22	6	6	2	8717.04946996466	6187.62720848057
					23	7	7	3		1.04646643109541	0.35	0.989929328621908	0.3		91.1418021201413	134.28574204947		9114.18021201413	6714.2871024735		23	7	7	3	9114.18021201413	6714.2871024735
					24	8	8	4		1.05	0.4	0.993462897526502	0.4		95.113109540636	144.818939929329		9511.3109540636	7240.94699646643		24	8	8	4	9511.3109540636	7240.94699646643
					25	9	1	1		1.05353356890459	0.45	0.968727915194346	0.1		92.6059717314488	130.521607773852		9260.59717314488	6526.08038869258		25	9	1	1	9260.59717314488	6526.08038869258
					26	10	2	2		1.05706713780919	0.5	0.97226148409894	0.2		96.5772791519435	141.05480565371		9657.72791519435	7052.74028268551		26	10	2	2	9657.72791519435	7052.74028268551
					27	11	3	3		1.06060070671378	0.55	0.975795053003533	0.3		100.548586572438	151.588003533569		10054.8586572438	7579.40017667845		27	11	3	3	10054.8586572438	7579.40017667845
					28	12	4	4		1.06413427561837	0.6	0.979328621908127	0.4		104.519893992933	162.121201413428		10451.9893992933	8106.06007067138		28	12	4	4	10451.9893992933	8106.06007067138
					29	13	5	1		1.06766784452297	0.65	0.982862190812721	0.1		103.491201413428	148.174399293286		10349.1201413428	7408.71996466431		29	13	5	1	10349.1201413428	7408.71996466431
					30	14	6	2		1.07120141342756	0.7	0.986395759717314	0.2		107.462508833922	158.707597173145		10746.2508833922	7935.37985865725		30	14	6	2	10746.2508833922	7935.37985865725
					31	15	7	3		1.07473498233216	0.75	0.989929328621908	0.3		111.433816254417	169.240795053004		11143.3816254417	8462.03975265018		31	15	7	3	11143.3816254417	8462.03975265018
					32	16	8	4		1.07826855123675	0.8	0.993462897526502	0.4		115.405123674912	179.773992932862		11540.5123674912	8988.69964664311		32	16	8	4	11540.5123674912	8988.69964664311